## SelectionData
Selection Table
flow rate, Q | [m³/h] | 200
throw, LT | [m] | 2
supply temperature, Ts | [°C] | 26
room temperature, Tr | [°C] | 26
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | WS230 | WS230 | WS230 | WS230 | WS230 | WS230 | WS230 | WS230
| Size | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500
condition 1
condition 2
condition 3
duct air velocity, Vduct | [m/s] | 7.3652 | 4.6755 | 2.8335 | 1.8043 | 1.1501 | 0.72202 | 0.44655 | 0.28522
effective air velocity, Veff | [m/s] | 19.4227 | 12.0538 | 7.1108 | 4.413 | 2.7387 | 1.6709 | 1.0027 | 0.62225
static pressure, DPs | [Pa] | 321.2295 | 144.9464 | 53.3766 | 19.4943 | 10.2881 | 2.2639 | 1.1929 | <1
total pressure, DPtot | [Pa] | 353.7773 | 158.0625 | 58.1938 | 21.4475 | 11.0817 | 2.5766 | 1.3126 | <1
throw velocity, vT @ LT | [m/s] | 0.71125 | 0.55725 | 0.42471 | 0.33162 | 0.25834 | 0.19887 | 0.15114 | 0.11644
critical distance | [m] | - | - | - | - | - | - | - | -
air temperature @ LT | [°C] | - | - | - | - | - | - | - | -
sound power, Lw | [dB(A)] | >55 | 53.9234 | 44.3544 | 34.5661 | 22.6213 | <20 | <20 | <20
sound pressure, Lp | [dB(A)] | >55 | 45.9234 | 36.3544 | 26.5661 | <20 | <20 | <20 | <20
Sound Spectrum
Lw [dB]
125 | [Hz] | - | < BGL | 44.4422 | 39.1543 | 33.7102 | - | - | -
250 | [Hz] | - | 42.9406 | 43.9419 | 36.9668 | 26.9662 | - | - | -
500 | [Hz] | - | 56.9108 | 44.4439 | 33.0327 | 20.2497 | - | - | -
1000 | [Hz] | - | 63.7625 | 41.7644 | 26.0703 | 13.3146 | - | - | -
2000 | [Hz] | - | 60.8888 | 37.5254 | 19.2486 | < BGL | - | - | -
4000 | [Hz] | - | 57.2128 | 31.9341 | 10.446 | < BGL | - | - | -
8000 | [Hz] | - | < BGL | < BGL | < BGL | < BGL | - | - | -
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | WS230 | WS230 | WS230 | WS230 | WS230 | WS230 | WS230 | WS230
|  | Size | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500
condition 1
condition 2
condition 3
THROW
|  | Ak [m²] | 0.0028603 | 0.004609 | 0.0078129 | 0.012589 | 0.020285 | 0.033248 | 0.055408 | 0.089281
|  | K1 [m] | 1.5108 | 1.5108 | 1.5108 | 1.5108 | 1.5108 | 1.5108 | 1.5108 | 1.5108
|  | X0 [m] | -0.20648 | -0.21857 | -0.23578 | -0.25576 | -0.28113 | -0.31464 | -0.35916 | -0.41239
PRESSURE LOSS
|  | A | 11.1528 | 17.0349 | 29.2288 | 45.7409 | 54.9847 | 132.9936 | 181.7339 | 346.3819
|  | B | 0.5001 | 0.49495 | 0.48353 | 0.49672 | 0.55395 | 0.49936 | 0.54294 | 0.5
|  | Aduct [m²] | 0.007543 | 0.011882 | 0.019607 | 0.030791 | 0.048305 | 0.076945 | 0.12441 | 0.19478
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
Ak [m²]
K2 [-]
X0 [m]
SOUND POWER, NR
|  | A | 27.516 | 20.6427 | 22.7615 | 25.5835 | 27.3999 | 31.4269 | 27.0957 | 24.4846
|  | B | -78.1691 | -59.5442 | -81.3974 | -105.8523 | -129.6526 | -174.2246 | -159.7813 | -149.1239
SOUND POWER, dB(A)
|  | A | 25.935 | 20.9635 | 23.4303 | 25.195 | 24.2827 | 30.3403 | 27.5477 | 25.7436
|  | B | -68.3071 | -57.1477 | -79.787 | -98.9249 | -106.0363 | -162.1191 | -157.2516 | -153.9341
SOUND POWER SPECTRUM
| at 125 Hz | A | 14.1838 |  | 13.2895 | 15.477 | 14.8108 | 24.053 | 21.8007 | 17.9292
|  | B | -26.5323 |  | -25.9699 | -42.8477 | -44.7621 | -116.2078 | -109.4885 | -90.8458
| at 250 Hz | A | 11.5756 | 9.3538 | 16.0138 | 17.7679 | 20.4663 | 20.9262 | 23.7348 | 17.2448
|  | B | -12.7018 | -6.6186 | -40.9043 | -57.173 | -81.471 | -99.1613 | -126.8348 | -86.2005
| at 500 Hz | A | 26.2159 | 25.4745 | 30.1502 | 27.6086 | 23.1874 | 29.4701 | 28.5213 | 25.5672
|  | B | -69.9639 | -78.0614 | -115.3012 | -113.2465 | -102.6044 | -158.7283 | -167.2948 | -155.6302
| at 1 kHz | A | 39.5888 | 38.4653 | 35.671 | 39.1462 | 30.7084 | 41.4035 | 35.3844 | 35.8694
|  | B | -127.9922 | -140.0388 | -147.2318 | -181.3388 | -149.3882 | -240.447 | -219.8662 | -237.884
| at 2 kHz | A | 43.196 | 44.9332 | 45.7552 | 45.2888 | 43.0023 | 54.4221 | 43.2476 | 46.7845
|  | B | -151.6483 | -177.1818 | -204.8999 | -220.7056 | -228.7282 | -332.0741 | -280.7905 | -325.2204
| at 4 kHz | A |  | 48.1982 | 56.9759 | 53.3863 | 51.4215 | 73.4885 | 52.4408 | 54.9451
|  | B |  | -198.1566 | -269.9422 | -272.4116 | -288.0909 | -467.581 | -358.0111 | -398.034
| at 8 kHz | A | [7 empty] | 3.5872
|  | B | [7 empty] | -12.194
END

## IntermediateCalcul (hidden)
Critical distance
Type | #REF! | #REF! | WS230 | WS230 | WS230 | WS230 | WS230 | WS230 | WS230 | WS230
Size | #REF! | #REF! | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500
condition 1 | #REF! | #REF!
condition 2 | #REF! | #REF!
condition 3 | #REF! | #REF!
A
dT
4 | #REF! | #REF!
6 | #REF! | #REF!
8 | #REF! | #REF!
10 | #REF! | #REF!
12 | #REF! | #REF!
B
4 | #REF! | #REF!
6 | #REF! | #REF!
8 | #REF! | #REF!
10 | #REF! | #REF!
12 | #REF! | #REF!
dT requested
0
dT1 | #REF! | #REF!
dT2 | #REF! | #REF!
A1 | #REF! | #REF!
A2 | #REF! | #REF!
B1 | #REF! | #REF!
B2 | #REF! | #REF!